This is a Word editable document.

Items listed are standard.  Add any additional requirements below warranty

Select the appropriate options and include option sheet or cut and paste them into the specification

Applied Calm 42 Packaged Terminal Air Conditioner / Heat Pump

SUGGESTED BID SPECIFICATIONS

The supplier will provide a packaged terminal air conditioner or heat pump of the sizes and capacities shown on the mechanical schedule and conforming to the listed specifications. Each unit shall consist of a chassis, wall case/sleeve, outside grille and room cabinet.

Units shall be design certified to the applicable standard, tested and listed by a nationally recognized testing laboratory.  The specified product shall be an Applied Comfort Ltd. Calm 42 models as listed on the schedule. The units shall be located as shown on the drawings.

Units shall be designed to operate on 208/230 volts, 60 Hz, single phase power.

Unit dimensions shall not exceed 42" wide and 16" high without optional air discharge package in place.

CHASSIS:

Unit chassis shall be a standard product of the manufacturer and shall be packed to prevent damage when reasonable care is exercised during shipment. Warnings on packaging shall alert handlers to the hazards of improper handling or stacking.

Chassis shall slide into a standard-sized wall case and, after installation and testing, be ready to operate. Each chassis shall consist of the following system and components, features.

• Refrigeration system constructed to isolate the hermetically sealed rotary-type compressor from external vibration. The system shall include copper/aluminum condenser and evaporator coils with capillary refrigerant control.

•  Drain Pan shall be polystyrene with a stainless steel insert, providing insulation and corrosion resistance by design.

• Air flow system consists of a three-speed room air motor for Hi, Med & Low A/C fan speeds.  Cycle switch to permit continuous indoor fan operation. The room air system incorporates a tangential crossflow blower wheel for reduced noise and increased efficiency.

• Condenser coils, shall be constructed of copper/aluminum and fins shall be bonded to tubes to prevent electrolytic action and shall be matched to provide the most efficient operation.

• Indoor and outdoor airflow which match the coil capacity for efficient transfer of heat. Design of the unit shall prevent water blow-off on the indoor evaporator coil. Indoor supply air grille, shall discharge air at an angle for improved circulation and to reduce interference with window treatments.

• Return air filter, constructed of washable media, that installs and removes without tools and without removing the room cover.

• Touch pad type digital control for selecting temperature set point, heating, cooling and  fan speed selection.

• Self-Diagnostics, The units on board control system shall incorporate a self-diagnostics system that will automatically clear some faults and display a “Fx” condition on the digital display to facilitate troubleshooting.

• Outside Air, The unit shall be supplied with a positive closing fresh air damper, located within the chassis. An accessible manual control shall operate the damper.

• Memory, in the event of a power loss the units memory shall maintain a record of set-point, mode, fan speed, on/off, and configuration and shall restart in the same operation as when power was lost.

• Random Compressor start, the unit shall have an automatic 2:45 to 3:15 restart delay to reduce excess demand on your building power supply after a power outage.

• Compressor Protection, to reduce compressor wear a random compressor start-up delay of 3 minutes and a minimum compressor run time of three minutes is featured.

• Automatic Freeze Protection, to prevent the room from freezing the unit will automatically turn on if power is present and the room temperature drops below 40 deg. F.

• Automatic Defrost, (heat pump) the unit will automatically switch to electric heat when the outdoor temperature drops below 35 deg F.

• Automatic quick warm-up, (heat pump) when room temp is 5 deg below set-point the unit will automatically switch to electric heat for the first cycle to bring the room up to set-point quickly.

WALL CASE/SLEEVE:

Wall case shall be insulated and shipped knocked-down and constructed of 18-gauge galvanized steel with a protective baked-on enamel finish. Base pan shall be 18-gauge galvanized. Cases shall be installed through exterior walls where shown on the plans and shall be level from side to side and front to back.  Case shall be secured to the wall at both sides as shown in installation instructions. In no instance shall fasteners be used through the base pan so as to protect the water integrity of the base pan.

OUTSIDE GRILLE / LOUVER:

A matching standard or architectural grille shall be supplied with the unit based on the requirements of the architect. Special grilles to be supplied by others must be submitted to the PTAC manufacturer for feasibility and air flow characteristics.

ROOM CABINET:

Each room chassis shall be equipped with a removable, wrap-around room cabinet constructed of a high impact polymer and incorporate the (2) return air filters.

SERVICE:

Bidders shall submit complete information regarding service availability, including address(es) and phone number(s), along with complete information of manufacturer address and phone number to cover service information pertinent to installed equipment.

RESPONSIBILITY FOR INSTALLATION, START-UP, TESTING, DEMONSTRATION:

Units shall be installed in full accordance to the manufacturer’s recommendation. The manufacturer shall not be liable for unit failure resulting from improper installation, which invalidates the warranty. Bidders shall specify their responsibilities for the initial starting of units,

performing necessary tests and adjustments to place units in proper operating condition and demonstrating heating and cooling operations to the owner or the owner’s representative.

WARRANTY:

There shall be a one-year limited warranty on labor and a five-year limited warranty on parts including the shipping fees.

Please check the option required.

If a custom color grille is required a color sample piece of trim/siding/brick/tile should be supplied for color matching.

OPTIONS:

42”  Stamped Grille – durable light-weight stamped aluminum grille

_____       ACC42SAGRILLE

_____       ACC42SAGRILLE – BEIGE

_____       ACC42SAGRILLE – CUSTOM COLOR

42” Architectural Grille – Extruded aluminum grille with high tensile rods.

_____       ACC42AAGRILLE-BEIGE

_____       ACC42AAGRILLE-SILVER

_____       ACC42AAGRILLE-CUSTOM COLOR

Drain Kit – drain tube & mounting plates

_____       ACC42drainkit

Duct Kit – Powder coated galvanized steel with poly insulation.  Designed to direct conditioned air left or right to an adjoining room.

_____        ACC42DUCTKIT

_____        ACC42DUCTEXTENSIONKIT

_____        ACC42DUCTTERMINATIONKIT

Sub-Base – 3” high powder coated galvanized steel, includes leveling legs and receptacle. Install with wall sleeve

_____         ACC42SUBBASE15-20

_____         ACC42SUBBASE30