DYNALINE Packaged Terminal Air Conditioner with Gas Heat

SUGGESTED BID SPECIFICATIONS

The supplier will provide packaged terminal gas heat/electric air conditioner of the sizes and capacities shown on the schedule and listed in the specifications. Each unit shall consist of a chassis, wall case/sleeve, outside grille and room cabinet.

Units shall be UL listed and/or C.S.A. design certified and shall be Suburban Manufacturing Company DYNALINE™ 3 models. The units shall be located as shown on the drawings.

Unit’s steady state efficiency shall be rated at 80% nominal and the EER of the air conditioner shall not be less than 10.0 EER.

Units shall be designed to operate on 208/230 volts, 60 Hz, single phase power.

Unit dimensions shall not exceed 42" wide and 16" high without optional air discharge package in place, and not more than 22-29/32" from face of room cabinet to face of standard exterior grille.

Units shall be designed to operate on Natural or LP gas for the heating cycle.

CHASSIS:

Unit chassis shall be a standard product of the manufacturer and shall be packed to prevent damage when reasonable care is exercised during shipment. Warnings on packaging shall alert handlers to the hazards of improper handling or stacking.

Chassis shall slide into a standard-sized wall case and, after installation and testing, be ready to operate. Each chassis shall consist of the following system and components:

• Refrigeration system constructed to isolate the hermetically sealed rotary-type compressor from external vibration. The system shall include copper/aluminum condenser and evaporator coils with capillary refrigerant control.

• Air flow system consists of a two-speed room air motor (for Hi & Low A/C and Hi & Low heat speeds) and a fan cycle switch to permit continuous indoor fan operation. A separate condenser fan operates in the A/C cycle only. The condenser fan, not operating in the heating mode, eliminates the potential for exhaust gases to be drawn back and freezing in the chassis compartment. The room air system incorporates a tangential blower wheel for reduced noise and increased efficiency.

• Condenser coils, with not less than 13 fins per inch, and evaporator coils, with not less than 11 fins per inch. Coils shall be constructed of copper/aluminum and fins shall be bonded to tubes to prevent electrolytic action.

• Indoor and outdoor airflow which match the coil capacity for efficient transfer of heat. Design of the unit shall prevent water blow-off on the indoor evaporator coil. Indoor supply air grille, constructed of extruded aluminum, shall discharge air at 52 degrees off vertical pattern.

• Electrostatic return air filter, constructed of washable media, that installs and removes without tools.

• Gas-fired heat exchanger, factory installed with electronic controlled, pilotless ignition system and a “draw-through” negative draft combustion air system. Gas ignition shall occur by energizing hot surface ignitor, which lights the burner on each thermostatically controlled heating cycle. Heat exchanger shall be located in indoor air stream so as not to be visible or accessible through indoor supply air grille.

• Touch pad digital control for selecting temperature set point, heating, cooling and manual fan operation. Control system to incorporate computerized self-diagnostics to facilitate troubleshooting.

• Outside air damper, positive closing and located within the chassis. An accessible manual control shall operate the damper.

• Compressor “lock-out” interface for use with standby emergency power generator.

WALL CASE:

Wall case shall be insulated and constructed of 18-gauge galvanized and shall have a protective baked-on enamel finish. Base pan shall be 18-gauge galvanized steel. Cases shall be installed through exterior walls where shown on the plans and shall be level from side to side and slope 1/4" from front to rear to ensure proper operation of condensate system. Case shall be secured to the wall at both sides as shown in installation instructions. In no instance shall fasteners be used through the base pan so as to protect the water integrity of the base pan.

OUTSIDE GRILLE:

Special grilles to be supplied by others must be submitted to the PTAC manufacturer for feasibility and air flow characteristics.

ROOM CABINET:

Each room chassis shall be equipped with a removable, wrap-around room cabinet constructed of 20-gauge steel with a protective baked-on enamel finish similar to the wall case.

GAS TYPE:

Natural gas units shall be equipped with a gas valve having a built-in regulator set to operate at the gas inlet supply pressure, minimum 5" W.C., maximum 7" W.C. Units burning LP gas shall be equipped with a gas valve having a built-in regulator set to operate at gas inlet supply pressures of 11" W.C. minimum and 13" W.C. maximum.

SERVICE:

Bidders shall submit complete information regarding service availability, including address(es) and phone number(s), along with complete information of manufacturer address and phone number to cover service information pertinent to installed equipment.

RESPONSIBILITY FOR INSTALLATION, START-UP, TESTING, DEMONSTRATION:

Units shall be installed in full accordance to the manufacturer’s recommendation. The manufacturer shall not be liable for unit failure resulting from improper installation, which invalidates the warranty. Bidders shall specify their responsibilities for the initial starting of units,

performing necessary tests and adjustments to place units in proper operating condition and demonstrating heating and cooling operations to the owner or the owner’s representative.

WARRANTY:

There shall be a one-year limited warranty on parts and labor and a five-year limited warranty on the compressor and heat exchanger.

OPTIONS

____    1657		Stamped Louver – clear anodized aluminum

____    1418		Architectural Aluminum Louver  - Dark Bronze Finish

____    1420		Architectural Aluminum Louver – Aluminum Finish

____    1651		Air Discharge Adapter – with grille 42” Length

____    1623		Extension for 1651 – with grille 42” Length

____    1624		Connector – 42” duct goes between adapter and extension

____    1664A		Rectangular Front for use with 1651 – DL3-0912 & Dl3-1220

____    1665A		Rectangular Front for use with1651 – DL3-1622

____    520547	2 lb Natural Gas Regulator

____    161198	Heat/Cool Manual Changeover Thermostat

____    520873	4” High Decorative Base Panel

____    520660	Adjustable Legs (2)

____    520992	Condensate Drain Kit