## Sheet1
1. Find the cooling capacity required
2. Find the heating capacity required
3. Highlight lines not required and use edit/delete/line to remove them
4. Edit the MARK column to reflect PTAC-1 thru ----------
5. Edit the AREA column to match your drawings or expand the schedule to show all rooms and their respective PTAC type
PACKAGED TERMINAL A/C MECHANICAL SCHEDULE - 277v
|  | SUPPLY |  | COOLING |  |  |  | HEATING | ELECTRICAL |  |  |  | APPLIED
|  | FAN |  | PERFORMANCE | [8 empty] | COMFORT
MARK | AREA | SUPPLY | SPEEDS | NOM | TOTAL | EER | DEHUMID | INPUT | VOLTAGE | TOTAL | MOP | WT | MODEL
|  | CFM |  | TONS | MBH |  | PTS/Hr | KW | PHASE | AMP |  | LBS | NUMBER
PTAC-1 | 110 | 294/277/260 | 3 | 0.63 | 7592 | 12 | 1.7 | 2 | 277 / 1 | 8.9 | 15 | 113 | A42EC07R-15
PTAC-2 | 120 | 294/277/260 | 3 | 0.63 | 7592 | 12 | 1.7 | 3 | 277 / 1 | 13.2 | 20 | 113 | A42EC07R-20
PTAC-3 | 210 | 294/277/260 | 3 | 0.75 | 9000 | 11.3 | 2.1 | 2 | 277 / 1 | 8.9 | 15 | 113 | A42EC09R-20
PTAC-4 | 220 | 294/277/260 | 3 | 0.75 | 9000 | 11.3 | 2.1 | 3 | 277 / 1 | 13.2 | 20 |  | A42EC09R-15
PTAC-5 | 310 | 312/294/277 | 3 | 1 | 12372 | 10.7 | 2.8 | 2 | 277 / 1 | 8 | 15 | 117 | A42EC12R-15
PTAC-6 | 320 | 312/294/277 | 3 | 1 | 12372 | 10.7 | 2.8 | 3 | 277 / 1 | 13.2 | 20 | 117 | A42EC12R-20
PTAC-7 | 330 | 312/294/277 | 3 | 1 | 12372 | 10.7 | 2.8 | 5 | 277 / 1 | 21.5 | 30 | 117 | A42EC12R-30
PTAC-8 | 410 | 341/324/306 | 3 | 1.24 | 15136 | 9.8 | 3.2 | 2 | 277 / 1 | 8 | 15 | 119 | A42EC15R-15
PTAC-9 | 420 | 341/324/306 | 3 | 1.24 | 15136 | 9.8 | 3.2 | 3 | 277 / 1 | 13.2 | 20 | 119 | A42EC15R-20
PTAC-10 | 430 | 341/324/306 | 3 | 1.24 | 15136 | 9.8 | 3.2 | 5 | 277 / 1 | 21.5 | 30 | 119 | A42EC15R-30