## Sheet1
1. Find the cooling capacity required
2. Find the heating capacity required
3. Highlight lines not required and use edit/delete/line to remove them
4. Edit the MARK column to reflect PTHP-1 thru ----------
5. Edit the AREA column to match your drawings or expand the schedule to show all rooms and their respective PTAC type
PACKAGED TERMINAL HEAT PUMP MECHANICAL SCHEDULE
|  | SUPPLY |  | COOLING |  |  |  | HEATING |  | ELECTRICAL |  |  |  | APPLIED
|  | FAN |  | PERFORMANCE |  |  |  | SECTION | [5 empty] | COMFORT
MARK | AREA | SUPPLY | SPEEDS | NOM | TOTAL | EER | DEHUMID | INPUT | C.O.P. | VOLTAGE | TOTAL | MOP | WT | MODEL
|  | CFM |  | TONS | MBH |  | PTS/Hr | KW |  | PHASE | AMP |  | LBS | NUMBER
PTHP-1 | 110 | 294/277/260 | 3 | 0.63 | 7.5 / 7.6 | 12.2 / 12.0 | 1.7 | 2 | 3.4 / 3.4 | 208/230-1 | 8.9/7.9 | 15 | 113 | A42HC07K-15
PTHP-2 | 120 | 294/277/260 | 3 | 0.63 | 7.5 / 7.6 | 12.2 / 12.0 | 1.7 | 3 | 3.4 / 3.4 | 208/230-1 | 13.2/12.2 | 20 | 113 | A42HC07K-20
PTHP-3 | 210 | 294/277/260 | 3 | 0.75 | 8.95/9.10 | 11.4 / 11.3 | 2.1 | 2 | 3.3 / 3.3 | 208/230-1 | 8.9/7.9 | 15 | 113 | A42HC09K-15
PTHP-4 | 220 | 294/277/260 | 3 | 0.75 | 8.95/9.10 | 11.4 / 11.3 | 2.1 | 3 | 3.3 / 3.3 | 208/230-1 | 13.2/12.2 | 20 | 113 | A42HC09K-20
PTHP-5 | 310 | 312/294/277 | 3 | 1 | 12.4 / 12.5 | 10.5 / 10.7 | 2.8 | 2 | 3.1 / 3.1 | 208/230-1 | 8.9/7.9 | 15 | 117 | A42HC12K-15
PTHP-6 | 320 | 312/294/277 | 3 | 1 | 12.4 / 12.5 | 10.5 / 10.7 | 2.8 | 3 | 3.1 / 3.1 | 208/230-1 | 13.2/12.2 | 20 | 117 | A42HC12K-20
PTHP-7 | 330 | 312/294/277 | 3 | 1 | 12.4 / 12.5 | 10.5 / 10.7 | 2.8 | 5 | 3.1 / 3.1 | 208/230-1 | 21.5/20.5 | 30 | 117 | A42HC12K-30
PTHP-8 | 410 | 341/324/306 | 3 | 1.24 | 14.9 / 16.6 | 9.7 / 9.8 | 3.2 | 2 | 2.9 / 2.9 | 208/230-1 | 8.9/7.9 | 15 | 119 | A42HC15K
PTHP-9 | 420 | 341/324/306 | 3 | 1.24 | 14.9 / 16.6 | 9.7 / 9.8 | 3.2 | 3 | 2.9 / 2.9 | 208/230-1 | 13.2/12.2 | 20 | 119 | A42HC15K
PTHP-10 | 440 | 341/324/306 | 3 | 1.24 | 14.9 / 16.6 | 9.7 / 9.8 | 3.2 | 5 | 2.9 / 2.9 | 208/230-1 | 21.5/20.5 | 30 | 119 | A42HC15K