## Sheet1
1. Find the cooling, heating required
2. Highlight lines not required and use edit/delete/line to remove them
3. Edit the MARK column to reflect UNIT-1 thru ----------
4. Edit the AREA column to match your drawings or expand the schedule to show all rooms and their respective UNIT type
DYNAPACK (H) Hi-Eff - THRU-WALL CENTRAL FURNACE-A/C MECHANICAL SCHEDULE - L.P. GAS
|  | COOLING | [6 empty] | HEATING |  |  |  |  | ELECTRICAL
[14 empty] | MOTORS | [5 empty] | SUBURBAN
MARK | AREA | TOTAL | NOM | EER/SEER | REFRIGERANT |  | RLA | LRA | GAS |  | BTU |  | Therm | SUPPLY | COND | COMB | VOLTAGE |  |  | MODEL
|  | MBH | TONS |  | TYPE | CHGE |  |  | TYPE | WC | INPUT | OUTPUT | EFF | FLA/HP/RPM | FLA/HP/RPM | FLA | PHASE | MCA | MOP | NUMBER
Unit 1 | 50 | 12000 | 1 | 10.2/11 | 410A | 35 | 5.2 | 25 | L.P. | 11"-13" | 39000 | 36700 | 92%+ | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230/1 | 10.9 | 15 | DYPA12AC1A039H-L
Unit 2 | 110 | 17500 | 1.5 | 10.6/12 | 410A | 40 | 8.3 | 43 | L.P. | 11"-13" | 39000 | 36700 | 92%+ | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230/1 | 14.8 | 20 | DYPA18AC1A039H-L
Unit 3 | 120 | 17500 | 1.5 | 10.6/12 | 410A | 40 | 8.3 | 43 | L.P. | 11"-13" | 52000 | 48900 | 92%+ | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 14.8 | 20 | DYPA18AC1A052H-L
Unit 4 | 210 | 25200 | 2 | 10.6/12.1 | 410A | 85 | 10.9 | 54 | L.P. | 11"-13" | 39000 | 36700 | 92%+ | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 18 | 25 | DYPA24AC1A039H-L
Unit 5 | 220 | 25200 | 2 | 10.6/12.1 | 410A | 85 | 10.9 | 54 |  | 11"-13" | 52000 | 48900 | 92%+ | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 18 | 25 | DYPA24AC1A052H-L
Unit 6 | 310 | 30200 | 2.5 | 10.7/12.35 | 410A | 96 | 13.1 | 74 | L.P. | 11"-13" | 39000 | 36700 | 92%+ | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 20.5 | 30 | DYPA30AC1A039H-L
Unit 7 | 320 | 30200 | 2.5 | 10.7/12.35 | 410A | 96 | 13.1 | 74 | L.P. | 11"-13" | 47500 | 38000 | 92%+ | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 20.5 | 30 | DYPA30AC1A052H-L
Unit 8 | 410 | 34800 | 3 | 10/11.5 | 410A | 96 | 16 | 88 | L.P. | 11"-13" | 39000 | 36700 | 92%+ | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 25.2 | 40 | DYPA36AC1A039H-L
Unit 9 | 420 | 34800 | 3 | 10/11.5 | 410A | 96 | 16 | 88 | L.P. | 11"-13" | 47500 | 38000 | 92%+ | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 25.2 | 40 | DYPA36AC1A052H-L
Available as Editable XCELL file at: www.superiorptacs.com - Select DynaPack then pick from Download List