## Sheet1
1. Find the cooling, heating required
2. Highlight lines not required and use edit/delete/line to remove them
3. Edit the MARK column to reflect UNIT-1 thru ----------
4. Edit the AREA column to match your drawings or expand the schedule to show all rooms and their respective UNIT type
DYNAPACK (S) Standard THRU-WALL CENTRAL FURNACE-A/C MECHANICAL SCHEDULE - L.P. GAS
|  | COOLING | [6 empty] | HEATING |  |  |  |  | ELECTRICAL
[14 empty] | MOTORS | [5 empty] | SUBURBAN
MARK | AREA | TOTAL | NOM | EER/ | REFRIGERANT |  | RLA | LRA | GAS |  | BTU |  | Therm | SUPPLY | COND | COMB | VOLTAGE |  |  | MODEL
|  | MBH | TONS | SEER | TYPE | CHGE |  |  | TYPE | WC | INPUT | OUTPUT | EFF | FLA/HP/RPM | FLA/HP/RPM | FLA | PHASE | MCA | MOP | NUMBER
UNIT-1 | 110 | 12000 | 1 | 10.2/11 | 410A | 35 | 5.2 | 25 | L.P. | 11" -13" | 35500 | 28400 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 11.5 | 15 | DYPA12AC1036L
UNIT-2 | 120 | 12000 | 1 | 10.2/11 | 410A | 35 | 5.2 | 25 | L.P. | 11" -13" | 47500 | 38000 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 11.5 | 20 | DYPA12AC1048L
UNIT-3 | 130 | 17000 | 1.5 | 10.6.12 | 410A | 40 | 8.3 | 43 | L.P. | 11" -13" | 35500 | 28400 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 13.2 | 20 | DYPA18AC1036L
UNIT-4 | 140 | 17000 | 1.5 | 10.6.12 | 410A | 40 | 8.3 | 43 | L.P. | 11" -13" | 47500 | 38000 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 13.2 | 20 | DYPA18AC1048L
UNIT-5 | 150 | 17000 | 1.5 | 10.6.12 | 410A | 40 | 8.3 | 43 | L.P. | 11" -13" | 59000 | 47200 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 13.2 | 20 | DYPA18AC1060L
UNIT-6 | 210 | 25200 | 2 | 10.6/12.1 | 410A | 85 | 10.9 | 54 | L.P. | 11" -13" | 35500 | 28400 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 16.9 | 25 | DYPA24AC1036L
UNIT-7 | 220 | 25200 | 2 | 10.6/12.1 | 410A | 85 | 10.9 | 54 | L.P. | 11" -13" | 47500 | 38000 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 16.9 | 25 | DYPA24AC1048L
UNIT-8 | 230 | 25200 | 2 | 10.6/12.1 | 410A | 85 | 10.9 | 54 | L.P. | 11" -13" | 59000 | 47200 | 82% | 4.0/.5/1050 | .9/.125/1075 | 0.9 | 208/230-1 | 16.9 | 25 | DYPA24AC1060L
UNIT-9 | 310 | 30200 | 2.5 | 10.7/12.35 | 410A | 96 | 13.1 | 74 | L.P. | 11" -13" | 35500 | 28400 | 82% | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 20.7 | 30 | DYPA30AC0136L
UNIT-10 | 320 | 30200 | 2.5 | 10.7/12.35 | 410A | 96 | 13.1 | 74 | L.P. | 11" -13" | 47500 | 38000 | 82% | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 20.7 | 30 | DYPA30AC0148L
UNIT-11 | 330 | 30200 | 2.5 | 10.7/12.35 | 410A | 96 | 13.1 | 74 | L.P. | 11" -13" | 59000 | 47200 | 82% | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 20.7 | 30 | DYPA30AC0160L
UNIT-12 | 410 | 34800 | 3 | 10/11.5 | 410A | 96 | 16 | 88 | L.P. | 11" -13" | 35500 | 28400 | 82% | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 25.2 | 40 | DYPA36AC0136L
UNIT-13 | 420 | 34800 | 3 | 10/11.5 | 410A | 96 | 16 | 88 | L.P. | 11" -13" | 47500 | 38000 | 82% | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 25.2 | 40 | DYPA36AC0148L
UNiT-14 | 430 | 34800 | 3 | 10/11.5 | 410A | 96 | 16 | 88 | L.P. | 11" -13" | 59000 | 47200 | 82% | 4.0/.5/1050 | 1.3/.25/1075 | 0.9 | 208/230-1 | 25.2 | 40 | DYPA36AC0160L
Available as Editable XCELL file at: www.superiorptacs.com - Select DynaPack then pick from Download List